## 1. Design Parameters

| Parameter | Value |
| --- | --- |
| Power Output | 25 MW |
| Rated Speed (RPM) | 3,000 RPM |
| Output Voltage | 11 kV |

## 2. Component Breakdown

### 2.1 Generator

- Type: Synchronous, 3-phase, brushless

- Rated Power: 25 MW

- Rated Voltage: 11 kV

- Frequency: 50 Hz

- Power Factor: 0.85 (lagging)

- Stator Winding: Class F insulation, copper windings

- Rotor: Forged steel, salient pole

- Bearings: Hydrodynamic, self-lubricated

- Enclosure: IP54

### 2.2 Turbine

- Type: Multi-stage, axial flow, condensing steam turbine

- Inlet Steam Pressure: 90 bar

- Inlet Steam Temperature: 540°C

- Exhaust Pressure: 0.1 bar (absolute)

- Blades: Stainless steel, precision machined

- Casing: Carbon steel, welded construction

- Governor: Electro-hydraulic, digital control

### 2.3 Excitation System

- Type: Static excitation, brushless

- Voltage Regulation: ±0.5%

- Response Time: < 0.2 seconds

- Redundancy: Dual-channel, automatic switchover

- Control Interface: Digital, SCADA compatible

## 3. Material Specifications

| Component | Material Specification |
| --- | --- |
| Stator Core | Laminated silicon steel, 0.5 mm |
| Rotor Shaft | Forged alloy steel (AISI 4140) |
| Turbine Blades | 17-4 PH stainless steel |
| Turbine Casing | ASTM A516 Grade 70 carbon steel |
| Bearings | Babbitt-lined steel |
| Windings | High-conductivity copper, Class F |
| Fasteners | High-tensile alloy steel, Grade 8.8 |

## 4. Control System Logic

- Startup Sequence:

  - Pre-lubrication check

  - Turbine warm-up and synchronization

  - Generator excitation ramp-up

  - Load acceptance and grid synchronization

- Shutdown Sequence:

  - Load shedding

  - Excitation ramp-down

  - Turbine cooldown

  - Lubrication post-run

- Protection Functions:

  - Over-speed trip

  - Over/under voltage protection

  - Overcurrent protection

  - Differential protection

  - Bearing temperature monitoring

  - Vibration monitoring

  - Emergency stop

- Control Interface:

  - HMI touchscreen panel

  - Remote SCADA integration

  - Data logging and event recording

## 5. Cooling Requirements

- Generator Cooling:

  - Type: Closed-loop water cooling

  - Water Flow Rate: 120 L/s

  - Inlet Water Temperature: ≤ 30°C

  - Outlet Water Temperature: ≤ 40°C

  - Heat Exchanger: Plate type, stainless steel

- Turbine Cooling:

  - Type: Direct steam and auxiliary water cooling

  - Auxiliary Water Flow Rate: 30 L/s

## 6. Performance Curves

### 6.1 Power Output vs. Efficiency

| Power Output (MW) | Efficiency (%) |
| --- | --- |
| 5 | 88.0 |
| 10 | 91.5 |
| 15 | 93.0 |
| 20 | 94.2 |
| 25 | 95.0 |

[Graph Placeholder: Power Output vs. Efficiency Curve]

### 6.2 Load vs. Terminal Voltage

| Load (%) | Terminal Voltage (kV) |
| --- | --- |
| 0 | 11.2 |
| 25 | 11.1 |
| 50 | 11.0 |
| 75 | 10.9 |
| 100 | 10.8 |

[Graph Placeholder: Load vs. Terminal Voltage Curve]

## 7. Expected Lifetime and Maintenance

- Expected Lifetime: 30 years

- Major Overhaul Interval: 40,000 operating hours